-08-

HT Section,

Electricity Department

30. 	This file relates to revision of HT bills for the months November 2025, December 2025 and January 2026 in respect of M/s. GVS Residency (Consumer No. 536), NH-214, Bypass Road, Yanam - 533464, with sanctioned demand of 160 KVA.

31. 	A communication has been received from the Assistant Engineer, Yanam Sub-Division vide letter No.1605/ED/AE/Y.F.7/2025-26 dated 27.02.2026.

In the said letter, it is informed that the consumer has requested for revision of HT bills for the months November 2025, December 2025 and January 2026, stating that the billed amounts are abnormally high despite low utilization.

32. 	The HT reading registers and reading statements for the above said months have been verified.

It is observed that during the month of November 2025, the MRT wing replaced the old energy meter with a new meter on 11.11.2025 at the consumer premises.

33. 	On verification of the readings, it is noticed that the Multiplying Factor (MF) has been erroneously taken as 400 instead of 200, which resulted in excess billing (double the actual consumption) for the months November - 2025, December - 2025 and January – 2026.

34. 	Due to the above error in MF, the consumer has been overcharged in all three months.

Further, it is reported that the consumer has already paid the HT bills for November 2025 and December 2025, as per payment particulars furnished.

35.	The corrected readings with proper MF (200) are furnished below:

#### November 2025

- Actual Units: 19,840 (instead of 32,160)

#### December 2025

- Actual Units: 19,160 (instead of 38,320)

#### January 2026

- Actual Units: 21,140 (instead of 42,280)

36. 	Hence, the HT bills for the months November 2025, December 2025 and January 2026 require revision based on correct MF (200).

The excess amount paid by the consumer may be adjusted in the forthcoming CC bills.

-09-

HT Section,

Electricity Department

(From pre-page)

Reading for November – 2025 (Meter Changed on 11.11.2025) (Changed Meter M.F = 400)

|  | Previous Reading | Present Reading | Difference | Multi Factor | Consumption |
| --- | --- | --- | --- | --- | --- |
| KWH | 20886.60 | 20918.10 | 31.50 | 200 | 6300 |
| KVAH | 22886.00 | 22923.60 | 37.60 | 200 | 7520 |
| KWH | 0.00 | 51.80 | 51.80 | 400 | 20720 |
| KVAH | 0.00 | 61.60 | 61.60 | 400 | 24640 |

Revised Readings for November – 2025 (Changed Meter M.F = 200)

|  | Previous Reading | Present Reading | Difference | Multi Factor | Consumption |
| --- | --- | --- | --- | --- | --- |
| KWH | 20886.60 | 20918.10 | 31.50 | 200 | 6300 |
| KVAH | 22886.00 | 22923.60 | 37.60 | 200 | 7520 |
| KWH | 0.00 | 51.80 | 51.80 | 200 | 10360 |
| KVAH | 0.00 | 61.60 | 61.60 | 200 | 12320 |

Total KVAH units for November 2025 = 7520 + 12320 = 19840

November - 2025 CC Bill

| CONSUMPTION DETAILS | BEFORE REVISION | AFTER REVISION |
| --- | --- | --- |
| KWH UNITS | 27020 | 16660 |
| KVAH UNITS | 32160 | 19840 |
| SANCTION DEMAND | 160 | 160 |
| REC. DEMAND | 128 | 64 |
| CHAR. DEMAND | 136 | 136 |
| EXCE.DEMAND | 0 | 0 |
| KVAH EXCESS | 0 | 0 |
| CLAIM DETAILS |  |  |
| UNIT CHARGE | 2,10,648 | 1,29,952 |
| DEM. CHARGE | 61,200 | 61,200 |
| OTHER CHARGE | 0 | 0 |
| EXE.KW. CHARGE | 0 | 0 |
| SURCHARGE | 27,185 | 19,115 |
| PROMPT PAY REB | 0 | 0 |
| BILL AMOUNT | 2,99,033 | 2,10,267 |

Reading for December – 2025 (Meter M.F = 400)

|  | Previous Reading | Present Reading | Difference | Multi Factor | Consumption |
| --- | --- | --- | --- | --- | --- |
| KWH | 51.80 | 131.10 | 79.30 | 400 | 31720 |
| KVAH | 61.60 | 157.40 | 95.80 | 400 | 38320 |

Revised Reading for December – 2025 (Meter M.F = 200)

|  | Previous Reading | Present Reading | Difference | Multi Factor | Consumption |
| --- | --- | --- | --- | --- | --- |
| KWH | 51.80 | 131.10 | 79.30 | 200 | 15860 |
| KVAH | 61.60 | 157.40 | 95.80 | 200 | 19160 |

-10-

HT Section,

Electricity Department

(From pre-page)

December - 2025 CC Bill

| CONSUMPTION DETAILS | BEFORE REVISION | AFTER REVISION |
| --- | --- | --- |
| KWH UNITS | 31720 | 15860 |
| KVAH UNITS | 38320 | 19160 |
| SANCTION DEMAND | 160 | 160 |
| REC. DEMAND | 124 | 62 |
| CHAR. DEMAND | 136 | 136 |
| EXCE.DEMAND | 0 | 0 |
| KVAH EXCESS | 0 | 0 |
| CLAIM DETAILS |  |  |
| UNIT CHARGE | 2,50,996 | 1,25,498 |
| DEM. CHARGE | 61,200 | 61,200 |
| OTHER CHARGE | 0 | 0 |
| EXE.KW. CHARGE | 0 | 0 |
| SURCHARGE | 31,220 | 18,670 |
| PROMPT PAY REB | 0 | 0 |
| BILL AMOUNT | 3,43,416 | 2,05,368 |

| MONTH | BEFORE REVISION | AFTER REVISION) | DIFFERENCE |
| --- | --- | --- | --- |
| November - 2025 | 2,99,033 | 2,10,267 | (+)88,766 |
| December - 2025 | 3,43,416 | 2,05,368 | (+)1,38,048 |
| Excess amount to be refunded = |  |  | (+)2,26,814 |

Reading for January – 2026 (Meter M.F = 400)

|  | Previous Reading | Present Reading | Difference | Multi Factor | Consumption |
| --- | --- | --- | --- | --- | --- |
| KWH | 131.10 | 219.40 | 88.30 | 400 | 35320 |
| KVAH | 157.40 | 263.10 | 105.70 | 400 | 42280 |

Revised Reading for January – 2026 (Meter M.F = 200)

|  | Previous Reading | Present Reading | Difference | Multi Factor | Consumption |
| --- | --- | --- | --- | --- | --- |
| KWH | 131.10 | 219.40 | 88.30 | 200 | 17660 |
| KVAH | 157.40 | 263.10 | 105.70 | 200 | 21140 |

January - 2026 CC Bill

| CONSUMPTION DETAILS | BEFORE REVISION | AFTER REVISION |
| --- | --- | --- |
| KWH UNITS | 35320 | 17660 |
| KVAH UNITS | 42280 | 21140 |
| SANCTION DEMAND | 160 | 160 |
| REC. DEMAND | 180 | 90 |
| CHAR. DEMAND | 180 | 136 |
| EXCE.DEMAND | 20 | 0 |
| KVAH EXCESS | 4698 | 0 |

-11-

HT Section,

Electricity Department

(From pre-page)

| CLAIM DETAILS |  |  |
| --- | --- | --- |
| UNIT CHARGE | 2,76,934 | 1,38,467 |
| DEM. CHARGE | 90,000 | 61,200 |
| OTHER CHARGE | 0 | 0 |
| EXE.KW. CHARGE | 30,772 | 0 |
| SURCHARGE | 39,771 | 19,967 |
| PROMPT PAY REB | 0 | 0 |
| BILL AMOUNT | 4,37,477 | 2,19,634 |

Excess in January – 2026 Bill Amount = 4,37,477- 2,19,634 = 2,17,843

November and December Bill payments

| Month | Paid Date | BPSC reflected month |
| --- | --- | --- |
| November - 2025 | 13.01.2026 | January |
| December - 2025 | 11.02.2026 | February |

BPSC Revision for the Payments of November and December - 2025

| Month | BPSC BEFORE REVISION | Revised Bill Amount | Number of Days Delay Payment | BPSC AFTER REVISION |
| --- | --- | --- | --- | --- |
| November - 2025 | 2,229 | 2,10,267 | 15 | 1,577 |
| December - 2025 | 2,576 | 2,05,368 | 15 | 1,540 |

37.	 Hence, the HT bills for the months November 2025, December 2025 and January 2026 require revision based on correct MF (200).

38. 	As per Clause 5.50 of JERC Supply Code, 2018. “Any excess/deficient payment made by the consumer shall be adjusted in the subsequent two bills.” Accordingly,

- The excess amount of ₹2,26,814  may be adjusted in the February – 2026 Current Consumption  Bill.

- The revised January 2026 CC bill shall be adjusted in the February 2026 bill along with applicable BPSC.

39. 	In view of the above, the file is submitted for approval to revise the HT bills for November 2025, December 2025 and January 2026 to adjust in the month of February 2026 Current Consumption Bill.

Supdt.(HT)

SAO-I  :

FC :

SE- cum-HOD :